## Slide 1: Wastewater Regionalization Preliminary Engineering Study
For the communities of
Harrisburg, Tea, and Worthing, SD
April 4, 2016
Presented by: Tanya Miller, PE
Joe Munson, PE
Banner Associates

## Slide 2: Communities Share a Common Problem
Each is outgrowing their wastewater treatment system and considering
  Expansion of their own system
  Regionalization with Sioux Falls
Another option to consider
  Regionalization with other communities

## Slide 3: Projected Wastewater Flows
Year | TEA |  | HARRISBURG |  | WORTHING |  | RURAL LINCOLN COUNTY |  | REGIONAL TOTAL | 
 | Pop. | Flow (gal/day) | Pop. | Flow (gal/day) | Pop. | Flow (gal/day) | Pop. | Flow (gal/day) | Average Day Flow (gal/day) | Peak Day Flow (gal/day)
2015 | 4,888 | 586,560 | 4,908 | 490,800 | 1,000 | 100,000 | 1,000 | 100,000 | 1,277,360 | 1,916,004
2020 | 6,359 | 763,080 | 5,971 | 597,100 | 1,217 | 121,700 | 1,338 | 133,800 | 1,615,680 | 2,423,508
2025 | 8,106 | 972,720 | 7,265 | 726,500 | 1,480 | 148,000 | 1,791 | 179,100 | 2,026,320 | 3,039,446
2030 | 9,874 | 1,184,880 | 8,839 | 883,900 | 1,801 | 180,100 | 2,397 | 239,700 | 2,488,580 | 3,732,735
2035 | 11,642 | 1,397,040 | 10,767 | 1,076,700 | 2,191 | 219,100 | 3,207 | 320,700 | 3,013,540 | 4,520,367
2040 | 13,400 | 1,608,000 | 13,100 | 1,310,000 | 2,666 | 266,600 | 4,292 | 429,200 | 3,613,800 | 5,420,543

## Slide 4: Treatment Alternatives Considered
Wastewater Plant near Worthing
  Discharging to the Beaver Creek
  Activated Sludge Process
Wastewater Plant east of Harrisburg
  Discharging to the Big Sioux River
  Sequencing Batch Reactor

## Slide 5: Pipeline Alternatives Considered

## Slide 6: Pipeline Alternatives Considered

## Slide 7: Phasing for Treatment Alternatives
Build plant to meet projected 2040 needs
Construct in two phases due to the significant population increase that is projected
  Phase I - Construct to meet 2030 needs
  Phase II - Plant expansion to meet 2040 needs
    Add treatment to meet anticipated nitrogen and phosphorus limits.

## Slide 8: Treatment Exhibit

## Slide 9: Treatment Exhibit

## Slide 10: Capital Cost for Regional Wastewater
 | SBR Phase I & II | SBR - No Phasing | Activated Sludge Phase I & II | Activated Sludge No Phasing
Treatment Plant Costs | $ 29,819,100 | $ 30,238,800 | $ 39,802,400 | $ 36,085,400
Force Main/ Outfall Costs | $ 22,316,600 | $ 22,316,600 | $ 16,575,300 | $ 16,575,300
Total Construction Costs | $ 52,135,700 | $ 52,555,400 | $ 56,377,700 | $ 52,660,700

## Slide 11: Are the WWTP costs realistic?
 | Peak Capacity (MGD) |  | Cost Adjusted to 2016 per ENR Index | Treatment Plant Construction Cost per Gallon
Regional WWTP Alternatives |  |  |  | 
SBR Phase I&II | 5.40 | $ 29,819,100 |  | $ 5.52
SBR - No Phasing | 5.40 | $ 30,238,800 |  | $ 5.60
Activated Sludge - Phase I&II | 5.40 | $ 39,802,400 |  | $ 7.37
Activated Sludge - No Phasing | 5.40 | $ 36,085,400 |  | $ 6.68
Lennox WWTP | 0.67 | $ 3,928,572 |  | $ 5.86
CostWorks Packaged WWTP | 5.00 | $ 30,750,000 |  | $ 6.15

## Slide 12: Intent of Study
Scope included comparing:
  Cost of regional wastewater plant
  Cost of regionalization with Sioux Falls
  Cost of recommended treatment alternative in each community’s report

## Slide 13: Sioux Falls Regionalization | Volume Charge
      Base charge = $15.60 per month
      Volume charge of $4.01 per 1,000 gallons
  Equalization credit = $0.44 per 1,000 gallons for 30 days of available storage
  Treatment credit of $0.55 per 1,000 gallons
      Rates and treatment credits were assumed to increase 3% annually to account for inflation.
$

## Slide 14: Sioux Falls Regionalization | SDC
WATER METER SIZE (INCH) | REGIONAL WASTEWATER SYSTEM DEVELOPMENT CHARGE (PER METER)
5/8” to 3/4” | $ 2,391
1” | $ 5,978
1 ½” | $ 11,954
2” | $ 19,127
3” | $ 35,863
4” | $ 60,000

## Slide 15: Sioux Falls Regionalization | Cost to Connect
Total Cost for Communities to Connect is $25.6 Million
WATER METER SIZE (INCH) | CITY OF HARRISBURG, SD |  | CITY OF TEA, SD |  | CITY OF WORTHING, SD | 
 | NUMBER OF METERS | SYSTEM DEVELOPMENT CHARGES | NUMBER OF METERS | SYSTEM DEVELOPMENT CHARGES | NUMBER OF METERS | SYSTEM DEVELOPMENT CHARGES
5/8” to 3/4” | 1,714 | $4,098,174 | 1,374 | $3,285,234 | 348 | $832,068
1” | 29 | $173,362 | 30 | $179,340 | 0 | $0
1 ½” | 11 | $131,494 | 53 | $633,562 | 0 | $0
2” | 21 | $401,667 | 10 | $191,270 | 2 | $38,254
3” | 3 | $107,589 | 2 | $71,726 | 0 | $0
4” | 1 | $60,000 | 7 | $420,000 | 0 | $0
Totals | 1,779 | $4,972,286 | 1,476 | $4,781,132 | 350 | $870,322
Additional Force Main Cost for Sioux Falls Connection/Extension |  | $3,736,736 |  | $6,530,879 |  | $4,721,500

## Slide 16: Recommended Alternatives in Prior Studies
Wastewater
Facility Plan
  Expansion of lagoons
  Lowest capital cost at $0.934 million (Jan. 2006)
Water/Wastewater Master Plan Update
  Regionalization with Sioux Falls
  Lowest capital cost at $10.18 million (March 2014)
Wastewater Facilities Plan
  Total Retention
  Lowest capital cost at $11.040 million (Dec. 2014) for a population of 10,353

## Slide 17: Challenges Comparing Costs
  Tea study didn’t include annual SDC costs in
  Sioux Falls regionalization option
    Report indicated that cost would be paid by developers
  Difficult to determine design flows from the Harrisburg Study
  Difficult to compare mechanical plant against lagoon system
    Mechanical plant achieves a much higher level of treatment

## Slide 18: Comparison of Capital Construction Costs
Chart: 
| Harrisburg | Tea | Worthing
SBR Phase I&II | 15562546.2248 | 19102234.4353 | 3167002.5403
SBR - No Phasing | 15788205.9545 | 19379220.2831 | 3212924.6489
Activated Sludge - Phase I&II | 20827069.9039 | 25564169.6518 | 4238341.3575
Activated Sludge - No Phasing | 18824697.7773 | 23106359.6484 | 3830855.4924
Recommended Alternative from Community's Study | 11314050.6643 | 11312010.7879 | 1242375.4723
Regionalization with Sioux Falls | 8709022.299 | 11312010.7879 | 5591822

## Slide 19: What can we compare?
Present worth Analysis Comparing
  Capital construction costs and O&M cost over 25 year planning period
    Regional treatment plant serving area communities from this study
    Regionalization with the City of Sioux Falls

## Slide 20: Present Worth Comparison
Chart: Wastewater Treatment Alternatives Capital Construction Costs and O&M Expenses
| Harrisburg | Tea | Worthing | Lincoln County | Overall
Sioux Falls Regionalization | 55275900 | 69944900 | 15055700 | 16829400 | 157105900
SBR Phase I&II | 38260680.5838 | 46963040.5981 | 7786108.4461 | 12535247.898 | 105545077.526
SBR - No Phasing | 39321088.7753 | 48264637.7519 | 8001903.1745 | 12882666.6933 | 108470296.395
Activated Sludge - Phase I&II | 41921164.8893 | 51456099.018 | 8531022.7376 | 13734522.9108 | 115642809.5557
Activated Sludge - No Phasing | 42814289.019 | 52552363.4891 | 8712774.8973 | 14027134.8612 | 118106562.2667
Regionalization - Tea and Harrisburg | 37941040.014 | 46570698.0462 | 0 | 0 | 84511738.0603

## Slide 21: Annual Cost | Harrisburg
20-Year on Equipment and 30-Year on Structures, Low Interest Loan
Chart: 
| 2015 | 2016 | 2017 | 2018 | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040
Debt Service - Regionalization with Area Communities | 1024751.7997 | 1024751.7997 | 1024751.7997 | 1024751.7997 | 1024751.7997 | 1024751.7997 | 1024751.7997 | 1024751.7997 | 1024751.7997 | 1024751.7997 | 1024751.7997 | 1024751.7997 | 1024751.7997 | 1024751.7997 | 1024751.7997 | 1095553.7107 | 1095553.7107 | 1095553.7107 | 1095553.7107 | 1095553.7107 | 682689.6647 | 682689.6647 | 682689.6647 | 682689.6647 | 682689.6647 | 682689.6647
O&M - Regionalization with Area Communities | 536177.4841 | 552262.8086 | 568830.6928 | 585895.6136 | 603472.482 | 621576.6565 | 640223.9562 | 659430.6749 | 679213.5951 | 699590.003 | 833186.6096 | 858182.2078 | 883927.6741 | 910445.5043 | 937758.8694 | 965891.6355 | 994868.3846 | 1024714.4361 | 1055455.8692 | 1087119.5453 | 1119733.1316 | 1153325.1256 | 1187924.8793 | 1223562.6257 | 1260269.5045 | 1298077.5896
Total Annual Costs - Sioux Falls Regionalization | 1170766.2727 | 1530410.2838 | 1476019.3791 | 1555161.5483 | 1611600.1418 | 1705478.3056 | 1768713.9532 | 1879172.3389 | 2010690.2898 | 2055735.4945 | 2192580.0547 | 2277373.7832 | 2419126.4523 | 2550827.9073 | 2772520.2536 | 2816381.39 | 3033688.7919 | 3179742.393 | 3561436.2274 | 3624426.579 | 3468027.4282 | 3671834.0367 | 4009393.3532 | 4214111.8911 | 4494584.4229 | 5350493.2138

## Slide 22: Summary
Regionalization with area communities is a viable solution for wastewater treatment
  It is more cost effective than regionalization with Sioux Falls
  It will likely be more cost effective for Tea and Harrisburg
  It may be cost effective for Worthing, depending on the WWTP location

## Slide 23: Recommendations
Further discussion on regionalization with area communities
Further study to review full cost of communities treating wastewater on their own
  Include life cycle analysis with O&M costs
  Compare alternatives on a present worth basis

## Slide 24: Thank you for your time
We welcome any questions you have

## Slide 25: Annual Cost per Customer | Harrisburg
Chart: 
| 2016 | 2017 | 2018 | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041
Annual Costs in 2016 Dollars for Sioux Falls Regionalization | 658.1036 | 827.1773 | 767.0955 | 777.1405 | 774.3691 | 787.9589 | 785.745 | 802.7074 | 825.8526 | 811.8789 | 832.6186 | 831.5563 | 849.3419 | 861.1361 | 899.9783 | 879.0537 | 910.4616 | 917.5912 | 988.2097 | 965.785 | 888.5673 | 904.6019 | 949.773 | 959.8732 | 984.3828 | 1126.7691
Annual Costs in 2016 Dollars for Regional Plant Serving Area Communities - Includes O&M | 877.4195 | 852.3666 | 828.1937 | 804.8677 | 782.3569 | 760.6307 | 739.6597 | 719.4155 | 699.8712 | 681.0004 | 705.5405 | 687.5312 | 670.1268 | 653.3049 | 637.0439 | 643.4218 | 627.3712 | 611.8544 | 596.8515 | 581.6073 | 461.8112 | 452.3251 | 443.1242 | 434.1984 | 425.5378 | 417.133

## Slide 26: Annual Cost per Customer | Tea
Chart: 
| 2016 | 2017 | 2018 | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041
Annual Costs in 2016 Dollars for Sioux Falls Regionalization | 968.7868 | 1203.9053 | 1121.6787 | 1139.4508 | 1108.9542 | 1142.9785 | 1120.5741 | 1164.8765 | 1151.574 | 1157.3947 | 1133.5683 | 1181.4389 | 1161.2374 | 1190.5718 | 1181.3851 | 1245.5376 | 1194.8552 | 1259.044 | 1249.4885 | 1297.0364 | 1158.9164 | 1223.7047 | 1233.6537 | 1270.5484 | 1281.8522 | 1340.2105
Annual Costs in 2016 Dollars for Regional Plant Serving Area Communities - Includes O&M | 1298.0768 | 1237.0006 | 1182.8447 | 1134.561 | 1091.3049 | 1052.3883 | 1008.8749 | 969.992 | 935.0935 | 903.6501 | 931.6935 | 904.7605 | 880.3345 | 858.1355 | 837.9251 | 848.647 | 830.8232 | 814.5246 | 799.613 | 785.9677 | 629.3285 | 622.444 | 616.0702 | 610.3827 | 605.3354 | 600.8876

## Slide 27: Annual Cost per Customer | Worthing
Chart: 
| 2016 | 2017 | 2018 | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041
Annual Costs in 2016 Dollars for Sioux Falls Regionalization | 1250.6521 | 1376.8972 | 1307.5994 | 1287.262 | 1275.0625 | 1257.7572 | 1248.3954 | 1233.9903 | 1233.6684 | 1221.9873 | 1217.8929 | 1258.0356 | 1213.4076 | 1206.9526 | 1207.7661 | 1209.749 | 1212.8876 | 1217.17 | 1268.5104 | 1234.8106 | 1160.4999 | 1177.777 | 1184.8931 | 1204.0503 | 1267.4369 | 1234.3121
Annual Costs in 2016 Dollars for Regional Plant Serving Area Communities - Includes O&M | 907.5759 | 881.6619 | 856.6582 | 832.5305 | 809.246 | 786.7731 | 765.0813 | 744.1414 | 723.9253 | 704.406 | 729.7895 | 711.1612 | 693.1586 | 675.7586 | 658.9387 | 665.5358 | 648.9336 | 632.8834 | 617.3649 | 602.3584 | 478.2881 | 468.4635 | 458.9343 | 449.6901 | 440.7205 | 432.0158

## Slide 28: How can we compare costs from community’s prior studies?
Capital construction costs per gallon of capacity
  Recommended alternative and mechanical treatment alternative from each community’s study
  Regional treatment plant from this study

## Slide 29: Comparison of Capital Construction Costs per Gallon of Capacity Provided
Chart: 
| Harrisburg | Tea | Worthing
SBR Phase I&II | 7.92 | 7.92 | 7.92
SBR - No Phasing | 8.0348 | 8.0348 | 8.0348
Activated Sludge - Phase I&II | 10.5991 | 10.5991 | 10.5991
Activated Sludge - No Phasing | 9.5801 | 9.5801 | 9.5801
Recommended Alternative from Community's Study | 7.0961 | 1.8853 | 5.4972
Mechancial Treatment from Community's Study | 16.7128 | 3.857

## Slide 30: Pipeline Alternatives Considered

## Slide 31: Pipeline Alternatives Considered

## Slide 32: Pipeline Alternatives Considered

## Slide 33: Pipeline Alternatives Considered

## Slide 34: Sioux Falls Regionalization | Annual Costs
Assumes a 3% annual increase in rates.
Chart: 
| 2015 | 2016 | 2017 | 2018 | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040
Harrisburg | 639692.8668 | 999336.8779 | 944945.9732 | 1024088.1425 | 1080526.7359 | 1174404.8998 | 1237640.5474 | 1348098.933 | 1479616.884 | 1524662.0886 | 1661506.6489 | 1746300.3773 | 1888053.0465 | 2019754.5015 | 2241446.8477 | 2285307.9842 | 2502615.3861 | 2648668.9871 | 3030362.8216 | 3093353.1731 | 3271169.7442 | 3474976.3527 | 3812535.6692 | 4017254.2071 | 4297726.7389 | 5153635.5298
Tea | 764504.208 | 1218491.5027 | 1189467.6449 | 1320083.2909 | 1365459.5116 | 1529309.6843 | 1604516.4566 | 1817161.4533 | 1910309.3393 | 2045440.8771 | 2109232.9371 | 2352554.2425 | 2424940.1854 | 2630129.5983 | 2730842.0315 | 3048260.3268 | 3024726.1344 | 3357398.5611 | 3460280.9355 | 3755770.4016 | 3825393.078 | 4181797.0579 | 4349071.5061 | 4621756.3411 | 4801469.4322 | 5173978.1803
Worthing | 130492.2 | 193954.562 | 187768.7844 | 199562.1133 | 214838.9446 | 228352.8292 | 245630.4021 | 261110.4501 | 283690.107 | 301508.0908 | 323736.5966 | 370604.7558 | 372710.5818 | 396146.6665 | 424774.9751 | 455305.2953 | 487864.4904 | 522588.0656 | 592183.2045 | 603309.858 | 641242.6379 | 690621.4739 | 734098.435 | 789937.7878 | 888352.4689 | 902929.1761

## Slide 35: Annual Cost | Tea
20-Year on Equipment and 30-Year on Structures, Low Interest Loan
Chart: 
| 2015 | 2016 | 2017 | 2018 | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040
Debt Service - Regionalization with Area Communities | 1257830.7452 | 1257830.7452 | 1257830.7452 | 1257830.7452 | 1257830.7452 | 1257830.7452 | 1257830.7452 | 1257830.7452 | 1257830.7452 | 1257830.7452 | 1257830.7452 | 1257830.7452 | 1257830.7452 | 1257830.7452 | 1257830.7452 | 1344736.4921 | 1344736.4921 | 1344736.4921 | 1344736.4921 | 1344736.4921 | 837966.8618 | 837966.8618 | 837966.8618 | 837966.8618 | 837966.8618 | 837966.8618
O&M - Regionalization with Area Communities | 658130.6074 | 677874.5256 | 698210.7614 | 719157.0842 | 740731.7968 | 762953.7507 | 785842.3632 | 809417.6341 | 833700.1631 | 858711.168 | 1022694.2117 | 1053375.0381 | 1084976.2892 | 1117525.5779 | 1151051.3453 | 1185582.8856 | 1221150.3722 | 1257784.8833 | 1295518.4298 | 1334383.9827 | 1374415.5022 | 1415647.9673 | 1458117.4063 | 1501860.9285 | 1546916.7564 | 1593324.259
Total Annual Costs - Sioux Falls Regionalization | 1429929.2862 | 1883916.5809 | 1854892.7231 | 1985508.3691 | 2030884.5898 | 2194734.7625 | 2269941.5348 | 2482586.5315 | 2575734.4175 | 2710865.9553 | 2774658.0153 | 3017979.3207 | 3090365.2636 | 3295554.6765 | 3396267.1097 | 3713685.405 | 3690151.2125 | 4022823.6393 | 4125706.0136 | 4421195.4798 | 4074129.8046 | 4430533.7845 | 4597808.2326 | 4870493.0676 | 5050206.1588 | 5422714.9069

## Slide 36: Annual Cost | Worthing
20-Year on Equipment and 30-Year on Structures, Low Interest Loan
Chart: 
| 2015 | 2016 | 2017 | 2018 | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040
Debt Service - Regionalization with Area Communities | 208538.5968 | 208538.5968 | 208538.5968 | 208538.5968 | 208538.5968 | 208538.5968 | 208538.5968 | 208538.5968 | 208538.5968 | 208538.5968 | 208538.5968 | 208538.5968 | 208538.5968 | 208538.5968 | 208538.5968 | 222946.8967 | 222946.8967 | 222946.8967 | 222946.8967 | 222946.8967 | 138928.4164 | 138928.4164 | 138928.4164 | 138928.4164 | 138928.4164 | 138928.4164
O&M - Regionalization with Area Communities | 109112.9581 | 112386.3468 | 115757.9372 | 119230.6754 | 122807.5956 | 126491.8235 | 130286.5782 | 134195.1755 | 138221.0308 | 142367.6617 | 169554.7805 | 174641.4239 | 179880.6666 | 185277.0866 | 190835.3992 | 196560.4612 | 202457.275 | 208530.9933 | 214786.9231 | 221230.5308 | 227867.4467 | 234703.4701 | 241744.5742 | 248996.9114 | 256466.8188 | 264160.8233
Total Annual Costs - Sioux Falls Regionalization | 437728.2356 | 501190.5976 | 495004.82 | 506798.1489 | 522074.9802 | 535588.8649 | 552866.4377 | 568346.4857 | 590926.1426 | 608744.1264 | 630972.6322 | 677840.7914 | 679946.6175 | 703382.7021 | 732011.0107 | 762541.3309 | 795100.526 | 829824.1012 | 899419.2401 | 910545.8936 | 889979.3644 | 939358.2004 | 982835.1615 | 1038674.5143 | 1137089.1954 | 1151665.9027